## Sheet1
Parameter | Original Address | Units | Length | Data Type
Meter Name | 29 | --- | 20 | UTF8
Meter Model | 49 | --- | 20 | UTF8
Manufacturer | 69 | --- | 20 | UTF8
Number of Phases | 2013 | --- | 1 | INT16U
Number of Wires | 2014 | --- | 1 | INT16U
Power System Configuration | 2015 | --- | 1 | INT16U
Nominal Frequency | 2016 | Hz | 1 | INT16U
Nominal Voltage | 2017 | V | 2 | FLOAT32
Nominal Current | 2019 | A | 2 | FLOAT32
Nominal Power Factor | 2021 | --- | 2 | FLOAT32
Normal Phase Rotation | 2023 | --- | 1 | INT16U
Active Energy Delivered (Into Load) | 2699 | kWh | 2 | FLOAT32
Active Energy Received (Out of Load) | 2701 | kWh | 2 | FLOAT32
Active Energy Delivered + Received | 2703 | kWh | 2 | FLOAT32
Active Energy Delivered- Received | 2705 | kWh | 2 | FLOAT32
Reactive Energy Delivered | 2707 | kVARh | 2 | FLOAT32
Reactive Energy Received | 2709 | kVARh | 2 | FLOAT32
Reactive Energy Delivered + Received | 2711 | kVARh | 2 | FLOAT32
Reactive Energy Delivered - Received | 2713 | kVARh | 2 | FLOAT32
Apparent Energy Delivered | 2715 | kVAh | 2 | FLOAT32
Apparent Energy Received | 2717 | kVAh | 2 | FLOAT32
Apparent Energy Delivered + Received | 2719 | kVAh | 2 | FLOAT32
Apparent Energy Delivered - Received | 2721 | kVAh | 2 | FLOAT32
Current A | 2999 | A | 2 | FLOAT32
Current B | 3001 | A | 2 | FLOAT32
Current C | 3003 | A | 2 | FLOAT32
Current N | 3005 | A | 2 | FLOAT32
Current G | 3007 | A | 2 | FLOAT32
Current Avg | 3009 | A | 2 | FLOAT32
Current Unbalance A | 3011 | % | 2 | FLOAT32
Current Unbalance B | 3013 | % | 2 | FLOAT32
Current Unbalance C | 3015 | % | 2 | FLOAT32
Current Unbalance Worst | 3017 | % | 2 | FLOAT32
Voltage A-B | 3019 | V | 2 | FLOAT32
Voltage B-C | 3021 | V | 2 | FLOAT32
Voltage C-A | 3023 | V | 2 | FLOAT32
Voltage L-L Avg | 3025 | V | 2 | FLOAT32
Voltage A-N | 3027 | V | 2 | FLOAT32
Voltage B-N | 3029 | V | 2 | FLOAT32
Voltage C-N | 3031 | V | 2 | FLOAT32
Voltage L-N Avg | 3035 | V | 2 | FLOAT32
Voltage Unbalance A-B | 3037 | % | 2 | FLOAT32
Voltage Unbalance B-C | 3039 | % | 2 | FLOAT32
Voltage Unbalance C-A | 3041 | % | 2 | FLOAT32
Voltage Unbalance L-L Worst | 3043 | % | 2 | FLOAT32
Voltage Unbalance A-N | 3045 | % | 2 | FLOAT32
Voltage Unbalance B-N | 3047 | % | 2 | FLOAT32
Voltage Unbalance C-N | 3049 | % | 2 | FLOAT32
Voltage Unbalance L-N Worst | 3051 | % | 2 | FLOAT32
Active Power A | 3053 | kW | 2 | FLOAT32
Active Power B | 3055 | kW | 2 | FLOAT32
Active Power C | 3057 | kW | 2 | FLOAT32
Active Power Total | 3059 | kW | 2 | FLOAT32
Reactive Power A | 3061 | kVAR | 2 | FLOAT32
Reactive Power B | 3063 | kVAR | 2 | FLOAT32
Reactive Power C | 3065 | kVAR | 2 | FLOAT32
Reactive Power Total | 3067 | kVAR | 2 | FLOAT32
Apparent Power A | 3069 | kVA | 2 | FLOAT32
Apparent Power B | 3071 | kVA | 2 | FLOAT32
Apparent Power C | 3073 | kVA | 2 | FLOAT32
Apparent Power Total | 3075 | kVA | 2 | FLOAT32
Power Factor A | 3077 |  | 2 | FLOAT32
Power Factor B | 3079 |  | 2 | FLOAT32
Power Factor C | 3081 |  | 2 | FLOAT32
Power Factor Total | 3083 |  | 2 | FLOAT32
Displacement Power Factor A | 3085 |  | 2 | FLOAT32
Displacement Power Factor B | 3087 |  | 2 | FLOAT32
Displacement Power Factor C | 3089 |  | 2 | FLOAT32
Displacement Power Factor Total | 3091 |  | 2 | FLOAT32
Frequency | 3109 | Hz | 2 | FLOAT32
Accumulated Energy Reset Date/Time | 3199 | --- | 4 | DATETIME
Active Energy Delivered (Into Load) | 3203 | Wh | 4 | INT64
Active Energy Received (Out of Load) | 3207 | Wh | 4 | INT64
Active Energy Delivered + Received | 3211 | Wh | 4 | INT64
Active Energy Delivered- Received | 3215 | Wh | 4 | INT64
Reactive Energy Delivered | 3219 | VARh | 4 | INT64
Reactive Energy Received | 3223 | VARh | 4 | INT64
Reactive Energy Delivered + Received | 3227 | VARh | 4 | INT64
Reactive Energy Delivered - Received | 3231 | VARh | 4 | INT64
Apparent Energy Delivered | 3235 | VAh | 4 | INT64
Apparent Energy Received | 3239 | VAh | 4 | INT64
Apparent Energy Delivered + Received | 3243 | VAh | 4 | INT64
Apparent Energy Delivered - Received | 3247 | VAh | 4 | INT64
THD Current A | 21299 | % | 2 | FLOAT32
THD Current B | 21301 | % | 2 | FLOAT32
THD Current C | 21303 | % | 2 | FLOAT32
THD Current N | 21305 | % | 2 | FLOAT32
THD Current G | 21307 | % | 2 | FLOAT32
THD Voltage A-B | 21321 | % | 2 | FLOAT32
THD Voltage B-C | 21323 | % | 2 | FLOAT32
THD Voltage C-A | 21325 | % | 2 | FLOAT32
THD Voltage L-L | 21327 | % | 2 | FLOAT32
THD Voltage A-N | 21329 | % | 2 | FLOAT32
THD Voltage B-N | 21331 | % | 2 | FLOAT32
THD Voltage C-N | 21333 | % | 2 | FLOAT32
THD Voltage L-N | 21337 | % | 2 | FLOAT32
Voltage A-B, H5 Magnitude, % | 21735 | % | 2 | FLOAT32
Voltage A-B, H7 Magnitude, % | 21747 | % | 2 | FLOAT32
Voltage B-C, H5 Magnitude, % | 22123 | % | 2 | FLOAT32
Voltage B-C, H7 Magnitude, % | 22135 | % | 2 | FLOAT32
Voltage C-A, H5 Magnitude, % | 22511 | % | 2 | FLOAT32
Voltage C-A, H7 Magnitude, % | 22523 | % | 2 | FLOAT32
Voltage A-N, H5 Magnitude, % | 22899 | % | 2 | FLOAT32
Voltage A-N, H7 Magnitude, % | 22911 | % | 2 | FLOAT32
Voltage B-N, H5 Magnitude, % | 23287 | % | 2 | FLOAT32
Voltage B-N, H7 Magnitude, % | 23299 | % | 2 | FLOAT32
Voltage C-N, H5 Magnitude, % | 23675 | % | 2 | FLOAT32
Voltage C-N, H7 Magnitude, % | 23687 | % | 2 | FLOAT32
Current A, H3 Magnitude, % | 24439 | % | 2 | FLOAT32
Current A, H5 Magnitude, % | 24451 | % | 2 | FLOAT32
Current A, H7 Magnitude, % | 24463 | % | 2 | FLOAT32
Current B, H3 Magnitude, % | 24827 | % | 2 | FLOAT32
Current B, H5 Magnitude, % | 24839 | % | 2 | FLOAT32
Current B, H7 Magnitude, % | 24851 | % | 2 | FLOAT32
Current C, H3 Magnitude, % | 25215 | % | 2 | FLOAT32
Current C, H5 Magnitude, % | 25227 | % | 2 | FLOAT32
Current C, H7 Magnitude, % | 25239 | % | 2 | FLOAT32
Min Current Avg | 42591 | A | 2 | FLOAT32
Min Voltage L-L Avg | 42597 | V | 2 | FLOAT32
Min Voltage L-N Avg | 42603 | V | 2 | FLOAT32
Min Active Power Total | 42609 | kW | 2 | FLOAT32
Min Reactive Power Total | 42615 | kVAR | 2 | FLOAT32
Min Apparent Power Total | 42621 | kVA | 2 | FLOAT32
Min Power Factor Total | 42627 |  | 2 | FLOAT32
Min Frequency | 42633 | Hz | 2 | FLOAT32
Max Current Avg | 42303 | A | 2 | FLOAT32
Max Voltage L-L Avg | 42309 | V | 2 | FLOAT32
Max Voltage L-N Avg | 42315 | V | 2 | FLOAT32
Max Active Power Total | 42321 | kW | 2 | FLOAT32
Max Reactive Power Total | 42327 | kVAR | 2 | FLOAT32
Max Apparent Power Total | 42333 | kVA | 2 | FLOAT32
Max Power Factor Total | 42339 | --- | 2 | FLOAT32
Max Frequency | 42345 | Hz | 2 | FLOAT32