## Sheet1
Parameter | Address | Length | Units | Data Type
Active Energy Delivered (Into Load) | 2699 | 2 | FLOAT32 | kWh
Active Energy Received (Out of Load) | 2701 | 2 | FLOAT32 | kWh
Active Energy Delivered + Received | 2703 | 2 | FLOAT32 | kWh
Active Energy Delivered- Received | 2705 | 2 | FLOAT32 | kWh
Reactive Energy Delivered | 2707 | 2 | FLOAT32 | kVARh
Reactive Energy Received | 2709 | 2 | FLOAT32 | kVARh
Reactive Energy Delivered + Received | 2711 | 2 | FLOAT32 | kVARh
Reactive Energy Delivered - Received | 2713 | 2 | FLOAT32 | kVARh
Apparent Energy Delivered | 2715 | 2 | FLOAT32 | kVAh
Apparent Energy Received | 2717 | 2 | FLOAT32 | kVAh
Apparent Energy Delivered + Received | 2719 | 2 | FLOAT32 | kVAh
Apparent Energy Delivered - Received | 2721 | 2 | FLOAT32 | kVAh
Active Energy in Quadrant I | 2723 | 2 | FLOAT32 | kWh
Active Energy in Quadrant II | 2725 | 2 | FLOAT32 | kWh
Active Energy in Quadrant III | 2727 | 2 | FLOAT32 | kWh
Active Energy in Quadrant IV | 2729 | 2 | FLOAT32 | kWh
Reactive Energy in Quadrant I | 2731 | 2 | FLOAT32 | kVARh
Reactive Energy in Quadrant II | 2733 | 2 | FLOAT32 | kVARh
Reactive Energy in Quadrant III | 2735 | 2 | FLOAT32 | kVARh
Reactive Energy in Quadrant IV | 2737 | 2 | FLOAT32 | kVARh
Apparent Energy in Quadrant I | 2739 | 2 | FLOAT32 | kVAh
Apparent Energy in Quadrant II | 2741 | 2 | FLOAT32 | kVAh
Apparent Energy in Quadrant III | 2743 | 2 | FLOAT32 | kVAh
Apparent Energy in Quadrant IV | 2745 | 2 | FLOAT32 | kVAh
Current A | 2999 | 2 | FLOAT32 | A
Current B | 3001 | 2 | FLOAT32 | A
Current C | 3003 | 2 | FLOAT32 | A
Current N | 3005 | 2 | FLOAT32 | A
Current G | 3007 | 2 | FLOAT32 | A
Current Avg | 3009 | 2 | FLOAT32 | A
Current Unbalance Worst | 3017 | 2 | FLOAT32 | ---
Voltage A-B | 3019 | 2 | FLOAT32 | V
Voltage B-C | 3021 | 2 | FLOAT32 | V
Voltage C-A | 3023 | 2 | FLOAT32 | V
Voltage L-L Avg | 3025 | 2 | FLOAT32 | V
Voltage A-N | 3027 | 2 | FLOAT32 | V
Voltage B-N | 3029 | 2 | FLOAT32 | V
Voltage C-N | 3031 | 2 | FLOAT32 | V
Voltage L-N Avg | 3035 | 2 | FLOAT32 | V
Voltage Unbalance L-N Worst | 3051 | 2 | FLOAT32 | ---
Active Power A | 3053 | 2 | FLOAT32 | W
Active Power B | 3055 | 2 | FLOAT32 | W
Active Power C | 3057 | 2 | FLOAT32 | W
Active Power Total | 3059 | 2 | FLOAT32 | W
Reactive Power A | 3061 | 2 | FLOAT32 | VAR
Reactive Power B | 3063 | 2 | FLOAT32 | VAR
Reactive Power C | 3065 | 2 | FLOAT32 | VAR
Reactive Power Total | 3067 | 2 | FLOAT32 | VAR
Apparent Power A | 3069 | 2 | FLOAT32 | VA
Apparent Power B | 3071 | 2 | FLOAT32 | VA
Apparent Power C | 3073 | 2 | FLOAT32 | VA
Apparent Power Total | 3075 | 2 | FLOAT32 | VA
Residual current I0 sum | 3093 | 2 | FLOAT32 | A
Frequency | 3109 | 2 | FLOAT32 | Hz
Power Factor A | 3143 | 2 | FLOAT32 | ---
Power Factor B | 3145 | 2 | FLOAT32 | ---
Power Factor C | 3147 | 2 | FLOAT32 | ---
Power Factor Total | 3149 | 2 | FLOAT32 | ---
Displacement Power Factor A | 3151 | 2 | FLOAT32 | ---
Displacement Power Factor B | 3153 | 2 | FLOAT32 | ---
Displacement Power Factor C | 3155 | 2 | FLOAT32 | ---
Displacement Power Factor Total | 3157 | 2 | FLOAT32 | ---
Power Factor A Lagging | 3159 | 2 | FLOAT32 | ---
Power Factor A Leading | 3161 | 2 | FLOAT32 | ---
Power Factor B Lagging | 3163 | 2 | FLOAT32 | ---
Power Factor B Leading | 3165 | 2 | FLOAT32 | ---
Power Factor C Lagging | 3167 | 2 | FLOAT32 | ---
Power Factor C Leading | 3169 | 2 | FLOAT32 | ---
Power Factor Lagging | 3171 | 2 | FLOAT32 | ---
Power Factor Leading | 3173 | 2 | FLOAT32 | ---
Current Disturbance | 13597 | 2 | INT32U
Voltage Disturbance | 13599 | 2 | INT32U
THD Current A | 21299 | 2 | FLOAT32 | %
THD Current B | 21301 | 2 | FLOAT32 | %
THD Current C | 21303 | 2 | FLOAT32 | %
THD Current N | 21305 | 2 | FLOAT32 | %
THD Voltage A-N | 21329 | 2 | FLOAT32 | %
THD Voltage B-N | 21331 | 2 | FLOAT32 | %
THD Voltage C-N | 21333 | 2 | FLOAT32 | %
K-Factor A | 21357 | 2 | FLOAT32
K-Factor B | 21359 | 2 | FLOAT32
K-Factor C | 21361 | 2 | FLOAT32
Crest Factor A | 21363 | 2 | FLOAT32 | ---
Crest Factor B | 21365 | 2 | FLOAT32 | ---
Crest Factor C | 21367 | 2 | FLOAT32 | ---
Crest Factor N | 21369 | 2 | FLOAT32 | ---
Total Cap HD Current A | 21431 | 2 | FLOAT32 | ---
Total Ind HD Current A | 21433 | 2 | FLOAT32 | ---
Total Cap HD Current B | 21435 | 2 | FLOAT32 | ---
Total Ind HD Current B | 21437 | 2 | FLOAT32 | ---
Total Cap HD Current C | 21439 | 2 | FLOAT32 | ---
Total Ind HD Current C | 21441 | 2 | FLOAT32 | ---
Total Cap HD Current N | 21443 | 2 | FLOAT32 | ---
Total Ind HD Current N | 21445 | 2 | FLOAT32 | ---
Total Cap HD Voltage A | 21451 | 2 | FLOAT32 | ---
Total Ind HD Voltage A | 21453 | 2 | FLOAT32 | ---
Total Cap HD Voltage B | 21455 | 2 | FLOAT32 | ---
Total Ind HD Voltage B | 21457 | 2 | FLOAT32 | ---
Total Cap HD Voltage C | 21459 | 2 | FLOAT32 | ---
Total Ind HD Voltage C | 21461 | 2 | FLOAT32 | ---
Total Even HD Current A | 21463 | 2 | FLOAT32 | ---
Total Odd HD Current A | 21465 | 2 | FLOAT32 | ---
Total Even HD Current B | 21467 | 2 | FLOAT32 | ---
Total Odd HD Current B | 21469 | 2 | FLOAT32 | ---
Total Even HD Current C | 21471 | 2 | FLOAT32 | ---
Total Odd HD Current C | 21473 | 2 | FLOAT32 | ---
Total Even HD Current N | 21475 | 2 | FLOAT32 | ---
Total Odd HD Current N | 21477 | 2 | FLOAT32 | ---
Total Even HD Voltage A | 21483 | 2 | FLOAT32 | ---
Total Odd HD Voltage A | 21485 | 2 | FLOAT32 | ---
Total Even HD Voltage B | 21487 | 2 | FLOAT32 | ---
Total Odd HD Voltage B | 21489 | 2 | FLOAT32 | ---
Total Even HD Voltage C | 21491 | 2 | FLOAT32 | ---
Total Odd HD Voltage C | 21493 | 2 | FLOAT32 | ---
Fundamental Active Power A | 21495 | 2 | FLOAT32 | W
Fundamental Active Power B | 21497 | 2 | FLOAT32 | W
Fundamental Active Power C | 21499 | 2 | FLOAT32 | W
Fundamental Active Power Total | 21501 | 2 | FLOAT32 | W
Fundamental Reactive Power A | 21503 | 2 | FLOAT32 | VAR
Fundamental Reactive Power B | 21505 | 2 | FLOAT32 | VAR
Fundamental Reactive Power C | 21507 | 2 | FLOAT32 | VAR
Fundamental Reactive Power Total | 21509 | 2 | FLOAT32 | VAR
Fundamental Apparent Power A | 21511 | 2 | FLOAT32 | VA
Fundamental Apparent Power B | 21513 | 2 | FLOAT32 | VA
Fundamental Apparent Power C | 21515 | 2 | FLOAT32 | VA
Fundamental Apparent Power Total | 21517 | 2 | FLOAT32 | VA
Current, Positive Sequence, Magnitude | 21597 | 2 | FLOAT32 | A
Current, Positive Sequence, Angle | 21599 | 2 | FLOAT32 | degrees
Current, Negative Sequence, Magnitude | 21601 | 2 | FLOAT32 | A
Current, Negative Sequence, Angle | 21603 | 2 | FLOAT32 | degrees
Current, Zero Sequence, Magnitude | 21605 | 2 | FLOAT32 | A
Current, Zero Sequence, Angle | 21607 | 2 | FLOAT32 | degrees
Voltage, Positive Sequence, Magnitude | 21609 | 2 | FLOAT32 | V
Voltage, Positive Sequence, Angle | 21611 | 2 | FLOAT32 | degrees
Voltage, Negative Sequence, Magnitude | 21613 | 2 | FLOAT32 | V
Voltage, Negative Sequence, Angle | 21615 | 2 | FLOAT32 | degrees
Voltage, Zero Sequence, Magnitude | 21617 | 2 | FLOAT32 | V
Voltage, Zero Sequence, Angle | 21619 | 2 | FLOAT32 | degrees
K-Factor N | 21677 | 2 | FLOAT32 | ---
Voltage A-N, H1 Magnitude, V | 22877 | 2 | FLOAT32 | V
Voltage A-N, H1 Angle | 22879 | 2 | FLOAT32 | degrees
Voltage A-N, H2 Magnitude, V | 22883 | 2 | FLOAT32 | V
Voltage A-N, H2 Angle | 22885 | 2 | FLOAT32 | degrees
Voltage A-N, H3 Magnitude, V | 22889 | 2 | FLOAT32 | V
Voltage A-N, H3 Angle | 22891 | 2 | FLOAT32 | degrees
Voltage A-N, H4 Magnitude, V | 22895 | 2 | FLOAT32 | V
Voltage A-N, H4 Angle | 22897 | 2 | FLOAT32 | degrees
Voltage A-N, H5 Magnitude, V | 22901 | 2 | FLOAT32 | V
Voltage A-N, H5 Angle | 22903 | 2 | FLOAT32 | degrees
Voltage B-N, H1 Magnitude, V | 23265 | 2 | FLOAT32 | V
Voltage B-N, H1 Angle | 23267 | 2 | FLOAT32 | degrees
Voltage B-N, H2 Magnitude, V | 23271 | 2 | FLOAT32 | V
Voltage B-N, H2 Angle | 23273 | 2 | FLOAT32 | degrees
Voltage B-N, H3 Magnitude, V | 23277 | 2 | FLOAT32 | V
Voltage B-N, H3 Angle | 23279 | 2 | FLOAT32 | degrees
Voltage B-N, H4 Magnitude, V | 23283 | 2 | FLOAT32 | V
Voltage B-N, H4 Angle | 23285 | 2 | FLOAT32 | degrees
Voltage B-N, H5 Magnitude, V | 23289 | 2 | FLOAT32 | V
Voltage B-N, H5 Angle | 23291 | 2 | FLOAT32 | degrees
Voltage C-N, H1 Magnitude, V | 23653 | 2 | FLOAT32 | V
Voltage C-N, H1 Angle | 23655 | 2 | FLOAT32 | degrees
Voltage C-N, H2 Magnitude, V | 23659 | 2 | FLOAT32 | V
Voltage C-N, H2 Angle | 23661 | 2 | FLOAT32 | degrees
Voltage C-N, H3 Magnitude, V | 23665 | 2 | FLOAT32 | V
Voltage C-N, H3 Angle | 23667 | 2 | FLOAT32 | degrees
Voltage C-N, H4 Magnitude, V | 23671 | 2 | FLOAT32 | V
Voltage C-N, H4 Angle | 23673 | 2 | FLOAT32 | degrees
Voltage C-N, H5 Magnitude, V | 23677 | 2 | FLOAT32 | V
Voltage C-N, H5 Angle | 23679 | 2 | FLOAT32 | degrees
Current A, H1 Magnitude, A | 24429 | 2 | FLOAT32 | A
Current A, H1 Angle | 24431 | 2 | FLOAT32 | degrees
Current A, H2 Magnitude, A | 24435 | 2 | FLOAT32 | A
Current A, H2 Angle | 24437 | 2 | FLOAT32 | degrees
Current A, H3 Magnitude, A | 24441 | 2 | FLOAT32 | A
Current A, H3 Angle | 24443 | 2 | FLOAT32 | degrees
Current A, H4 Magnitude, A | 24447 | 2 | FLOAT32 | A
Current A, H4 Angle | 24449 | 2 | FLOAT32 | degrees
Current A, H5 Magnitude, A | 24453 | 2 | FLOAT32 | A
Current A, H5 Angle | 24455 | 2 | FLOAT32 | degrees
Current A, H6 Magnitude, A | 24459 | 2 | FLOAT32 | A
Current A, H6 Angle | 24461 | 2 | FLOAT32 | degrees
Current A, H7 Magnitude, A | 24465 | 2 | FLOAT32 | A
Current A, H7 Angle | 24467 | 2 | FLOAT32 | degrees
Current B, H1 Magnitude, A | 24817 | 2 | FLOAT32 | A
Current B, H1 Angle | 24819 | 2 | FLOAT32 | degrees
Current B, H2 Magnitude, A | 24823 | 2 | FLOAT32 | A
Current B, H2 Angle | 24825 | 2 | FLOAT32 | degrees
Current B, H3 Magnitude, A | 24829 | 2 | FLOAT32 | A
Current B, H3 Angle | 24831 | 2 | FLOAT32 | degrees
Current B, H4 Magnitude, A | 24835 | 2 | FLOAT32 | A
Current B, H4 Angle | 24837 | 2 | FLOAT32 | degrees
Current B, H5 Magnitude, A | 24841 | 2 | FLOAT32 | A
Current B, H5 Angle | 24843 | 2 | FLOAT32 | degrees
Current B, H6 Magnitude, A | 24847 | 2 | FLOAT32 | A
Current B, H6 Angle | 24849 | 2 | FLOAT32 | degrees
Current B, H7 Magnitude, A | 24853 | 2 | FLOAT32 | A
Current B, H7 Angle | 24855 | 2 | FLOAT32 | degrees
Current C, H1 Magnitude, A | 25205 | 2 | FLOAT32 | A
Current C, H1 Angle | 25207 | 2 | FLOAT32 | degrees
Current C, H2 Magnitude, A | 25211 | 2 | FLOAT32 | A
Current C, H2 Angle | 25213 | 2 | FLOAT32 | degrees
Current C, H3 Magnitude, A | 25217 | 2 | FLOAT32 | A
Current C, H3 Angle | 25219 | 2 | FLOAT32 | degrees
Current C, H4 Magnitude, A | 25223 | 2 | FLOAT32 | A
Current C, H4 Angle | 25225 | 2 | FLOAT32 | degrees
Current C, H5 Magnitude, A | 25229 | 2 | FLOAT32 | A
Current C, H5 Angle | 25231 | 2 | FLOAT32 | degrees
Current C, H6 Magnitude, A | 25235 | 2 | FLOAT32 | A
Current C, H6 Angle | 25237 | 2 | FLOAT32 | degrees
Current C, H7 Magnitude, A | 25241 | 2 | FLOAT32 | A
Current C, H7 Angle | 25243 | 2 | FLOAT32 | degrees
Min Current A | 27217 | 2 | FLOAT32 | A
Min Current B | 27219 | 2 | FLOAT32 | A
Min Current C | 27221 | 2 | FLOAT32 | A
Min Current N | 27223 | 2 | FLOAT32 | A
Min Current G | 27225 | 2 | FLOAT32 | A
Min Current Avg | 27227 | 2 | FLOAT32 | A
Min Voltage A-B | 27237 | 2 | FLOAT32 | V
Min Voltage B-C | 27239 | 2 | FLOAT32 | V
Min Voltage C-A | 27241 | 2 | FLOAT32 | V
Min Voltage L-L Avg | 27243 | 2 | FLOAT32 | V
Min Voltage A-N | 27245 | 2 | FLOAT32 | V
Min Voltage B-N | 27247 | 2 | FLOAT32 | V
Min Voltage C-N | 27249 | 2 | FLOAT32 | V
Min Voltage L-N Avg | 27253 | 2 | FLOAT32 | V
Min Voltage Unbalance L-N Worst | 27269 | 2 | FLOAT32 | %
Min Active Power Total | 27277 | 2 | FLOAT32 | W
Min Reactive Power Total | 27285 | 2 | FLOAT32 | VAR
Min Apparent Power Total | 27293 | 2 | FLOAT32 | VA
Min Power Factor Lagging | 27321 | 2 | FLOAT32 | %
Min Power Factor Leading | 27323 | 2 | FLOAT32 | %
Min THD Current A | 27337 | 2 | FLOAT32 | %
Min THD Current B | 27339 | 2 | FLOAT32 | %
Min THD Current C | 27341 | 2 | FLOAT32 | %
Min THD Current N | 27343 | 2 | FLOAT32 | %
Min THD Voltage A-N | 27367 | 2 | FLOAT32 | %
Min THD Voltage B-N | 27369 | 2 | FLOAT32 | %
Min THD Voltage C-N | 27371 | 2 | FLOAT32 | %
Min Frequency | 27615 | 2 | FLOAT32 | Hz
Current A Low | 27643 | 2 | FLOAT32 | A
Current B Low | 27645 | 2 | FLOAT32 | A
Current C Low | 27647 | 2 | FLOAT32 | A
Current N Low | 27649 | 2 | FLOAT32 | A
Current Avg Low | 27651 | 2 | FLOAT32 | A
Voltage A-B Low | 27653 | 2 | FLOAT32 | V
Voltage B-C Low | 27655 | 2 | FLOAT32 | V
Voltage C-A Low | 27657 | 2 | FLOAT32 | V
Voltage L-L Avg Low | 27659 | 2 | FLOAT32 | V
Voltage Unbalance Low | 27669 | 2 | FLOAT32 | %
Frequency High | 28171 | 2 | FLOAT32 | Hz
Current A K Factor High | 28173 | 2 | FLOAT32 | ---
Current B K Factor High | 28175 | 2 | FLOAT32 | ---
Current C K Factor High | 28177 | 2 | FLOAT32 | ---
Current A Mean | 28179 | 2 | FLOAT32 | A
Current B Mean | 28181 | 2 | FLOAT32 | A
Current C Mean | 28183 | 2 | FLOAT32 | A
Current N Mean | 28185 | 2 | FLOAT32 | A
Current Avg Mean | 28187 | 2 | FLOAT32 | A
Voltage A-B Mean | 28189 | 2 | FLOAT32 | V
Voltage B-C Mean | 28191 | 2 | FLOAT32 | V
Voltage C-A Mean | 28193 | 2 | FLOAT32 | V
Voltage L-L Avg Mean | 28195 | 2 | FLOAT32 | V
Voltage Unbalance Mean | 28205 | 2 | FLOAT32 | ---
Active Power Mean | 28207 | 2 | FLOAT32 | W
Reactive Power Mean | 28209 | 2 | FLOAT32 | VAR
Apparent Power Mean | 28211 | 2 | FLOAT32 | VA
Power Factor Lagging Mean | 28213 | 2 | FLOAT32 | ---
Power Factor Leading Mean | 28215 | 2 | FLOAT32 | ---
Frequency Mean | 28217 | 2 | FLOAT32 | Hz
V1-Dip A1 | 40245 | 1 | INT16U
V1-Dip B1 | 40246 | 1 | INT16U
V1-Dip C1 | 40247 | 1 | INT16U
V1-Dip D1 | 40248 | 1 | INT16U
V1-Dip A2 | 40249 | 1 | INT16U
V1-Dip B2 | 40250 | 1 | INT16U
V1-Dip C2 | 40251 | 1 | INT16U
V1-Dip D2 | 40252 | 1 | INT16U
V1-Dip A3 | 40253 | 1 | INT16U
V1-Dip B3 | 40254 | 1 | INT16U
V1-Dip C3 | 40255 | 1 | INT16U
V1-Dip D3 | 40256 | 1 | INT16U
V1-Dip A4 | 40257 | 1 | INT16U
V1-Dip B4 | 40258 | 1 | INT16U
V1-Dip C4 | 40259 | 1 | INT16U
V1-Dip D4 | 40260 | 1 | INT16U
V1-Dip A5 | 40261 | 1 | INT16U
V1-Dip B5 | 40262 | 1 | INT16U
V1-Dip C5 | 40263 | 1 | INT16U
V1-Dip D5 | 40264 | 1 | INT16U
V1-Dip X1 | 40265 | 1 | INT16U
V1-Dip X2 | 40266 | 1 | INT16U
V1-Dip X3 | 40267 | 1 | INT16U
V1-Dip X4 | 40268 | 1 | INT16U
V1-Dip X5 | 40269 | 1 | INT16U
V2-Dip A1 | 40270 | 1 | INT16U
V2-Dip B1 | 40271 | 1 | INT16U
V2-Dip C1 | 40272 | 1 | INT16U
V2-Dip D1 | 40273 | 1 | INT16U
V2-Dip A2 | 40274 | 1 | INT16U
V2-Dip B2 | 40275 | 1 | INT16U
V2-Dip C2 | 40276 | 1 | INT16U
V2-Dip D2 | 40277 | 1 | INT16U
V2-Dip A3 | 40278 | 1 | INT16U
V2-Dip B3 | 40279 | 1 | INT16U
V2-Dip C3 | 40280 | 1 | INT16U
V2-Dip D3 | 40281 | 1 | INT16U
V2-Dip A4 | 40282 | 1 | INT16U
V2-Dip B4 | 40283 | 1 | INT16U
V2-Dip C4 | 40284 | 1 | INT16U
V2-Dip D4 | 40285 | 1 | INT16U
V2-Dip A5 | 40286 | 1 | INT16U
V2-Dip B5 | 40287 | 1 | INT16U
V2-Dip C5 | 40288 | 1 | INT16U
V2-Dip D5 | 40289 | 1 | INT16U
V2-Dip X1 | 40290 | 1 | INT16U
V2-Dip X2 | 40291 | 1 | INT16U
V2-Dip X3 | 40292 | 1 | INT16U
V2-Dip X4 | 40293 | 1 | INT16U
V2-Dip X5 | 40294 | 1 | INT16U
V3-Dip A1 | 40295 | 1 | INT16U
V3-Dip B1 | 40296 | 1 | INT16U
V3-Dip C1 | 40297 | 1 | INT16U
V3-Dip D1 | 40298 | 1 | INT16U
V3-Dip A2 | 40299 | 1 | INT16U
V3-Dip B2 | 40300 | 1 | INT16U
V3-Dip C2 | 40301 | 1 | INT16U
V3-Dip D2 | 40302 | 1 | INT16U
V3-Dip A3 | 40303 | 1 | INT16U
V3-Dip B3 | 40304 | 1 | INT16U
V3-Dip C3 | 40305 | 1 | INT16U
V3-Dip D3 | 40306 | 1 | INT16U
V3-Dip A4 | 40307 | 1 | INT16U
V3-Dip B4 | 40308 | 1 | INT16U
V3-Dip C4 | 40309 | 1 | INT16U
V3-Dip D4 | 40310 | 1 | INT16U
V3-Dip A5 | 40311 | 1 | INT16U
V3-Dip B5 | 40312 | 1 | INT16U
V3-Dip C5 | 40313 | 1 | INT16U
V3-Dip D5 | 40314 | 1 | INT16U
V3-Dip X1 | 40315 | 1 | INT16U
V3-Dip X2 | 40316 | 1 | INT16U
V3-Dip X3 | 40317 | 1 | INT16U
V3-Dip X4 | 40318 | 1 | INT16U
V3-Dip X5 | 40319 | 1 | INT16U
V1-Ovrvlt S1 | 40320 | 1 | INT16U
V1-Ovrvlt T1 | 40321 | 1 | INT16U
V1-Ovrvlt S2 | 40322 | 1 | INT16U
V1-Ovrvlt T2 | 40323 | 1 | INT16U
V1-Ovrvlt S3 | 40324 | 1 | INT16U
V1-Ovrvlt T3 | 40325 | 1 | INT16U
V1-Ovrvlt S4 | 40326 | 1 | INT16U
V1-Ovrvlt T4 | 40327 | 1 | INT16U
V2-Ovrvlt S1 | 40328 | 1 | INT16U
V2-Ovrvlt T1 | 40329 | 1 | INT16U
V2-Ovrvlt S2 | 40330 | 1 | INT16U
V2-Ovrvlt T2 | 40331 | 1 | INT16U
V2-Ovrvlt S3 | 40332 | 1 | INT16U
V2-Ovrvlt T3 | 40333 | 1 | INT16U
V2-Ovrvlt S4 | 40334 | 1 | INT16U
V2-Ovrvlt T4 | 40335 | 1 | INT16U
V3-Ovrvlt S1 | 40336 | 1 | INT16U
V3-Ovrvlt T1 | 40337 | 1 | INT16U
V3-Ovrvlt S2 | 40338 | 1 | INT16U
V3-Ovrvlt T2 | 40339 | 1 | INT16U
V3-Ovrvlt S3 | 40340 | 1 | INT16U
V3-Ovrvlt T3 | 40341 | 1 | INT16U
V3-Ovrvlt S4 | 40342 | 1 | INT16U
V3-Ovrvlt T4 | 40343 | 1 | INT16U
V1-Intrpt N1 | 40344 | 1 | INT16U
V1-Intrpt N2 | 40345 | 1 | INT16U
V1-Intrpt N3 | 40346 | 1 | INT16U
V2-Intrpt N1 | 40347 | 1 | INT16U
V2-Intrpt N2 | 40348 | 1 | INT16U
V2-Intrpt N3 | 40349 | 1 | INT16U
V3-Intrpt N1 | 40350 | 1 | INT16U
V3-Intrpt N2 | 40351 | 1 | INT16U
V3-Intrpt N3 | 40352 | 1 | INT16U
V-Swell S1 | 40436 | 1 | INT16U
V-Swell T1 | 40437 | 1 | INT16U
V-Swell S2 | 40438 | 1 | INT16U
V-Swell T2 | 40439 | 1 | INT16U
V-Swell S3 | 40440 | 1 | INT16U
V-Swell T3 | 40441 | 1 | INT16U
V-Swell S4 | 40442 | 1 | INT16U
V-Swell T4 | 40443 | 1 | INT16U
V-Intrpt N1 | 40444 | 1 | INT16U
V-Intrpt N2 | 40445 | 1 | INT16U
V-Intrpt N3 | 40446 | 1 | INT16U
V-Intrpt tot | 40447 | 1 | INT16U
V-Dip A1 | 40461 | 1 | INT16U
V-Dip B1 | 40462 | 1 | INT16U
V-Dip C1 | 40463 | 1 | INT16U
V-Dip D1 | 40464 | 1 | INT16U
V-Dip A2 | 40465 | 1 | INT16U
V-Dip B2 | 40466 | 1 | INT16U
V-Dip C2 | 40467 | 1 | INT16U
V-Dip D2 | 40468 | 1 | INT16U
V-Dip A3 | 40469 | 1 | INT16U
V-Dip B3 | 40470 | 1 | INT16U
V-Dip C3 | 40471 | 1 | INT16U
V-Dip D3 | 40472 | 1 | INT16U
V-Dip A4 | 40473 | 1 | INT16U
V-Dip B4 | 40474 | 1 | INT16U
V-Dip C4 | 40475 | 1 | INT16U
V-Dip D4 | 40476 | 1 | INT16U
V-Dip A5 | 40477 | 1 | INT16U
V-Dip B5 | 40478 | 1 | INT16U
V-Dip C5 | 40479 | 1 | INT16U
V-Dip D5 | 40480 | 1 | INT16U
V-Dip X1 | 40481 | 1 | INT16U
V-Dip X2 | 40482 | 1 | INT16U
V-Dip X3 | 40483 | 1 | INT16U
V-Dip X4 | 40484 | 1 | INT16U
V-Dip X5 | 40485 | 1 | INT16U
V1-Hrm Z | 43727 | 1 | INT16U | ---
V1-Hrm Z1 | 43728 | 1 | INT16U | ---
V1-Hrm Z2 | 43729 | 1 | INT16U | ---
V2-Hrm Z | 43730 | 1 | INT16U | ---
V2-Hrm Z1 | 43731 | 1 | INT16U | ---
V2-Hrm Z2 | 43732 | 1 | INT16U | ---
V3-Hrm Z | 43733 | 1 | INT16U | ---
V3-Hrm Z1 | 43734 | 1 | INT16U | ---
V3-Hrm Z2 | 43735 | 1 | INT16U | ---
V-Hrm Z1 | 43736 | 1 | INT16U | ---
V-Hrm Z2 | 43737 | 1 | INT16U | ---
V-Hrm Z Comp | 43738 | 2 | FLOAT32 | %
V-THD Z Comp | 43740 | 2 | FLOAT32 | %
I1-Hrm Z | 43742 | 1 | INT16U | ---
I1-Hrm Z1 | 43743 | 1 | INT16U | ---
I1-Hrm Z2 | 43744 | 1 | INT16U | ---
I2-Hrm Z | 43745 | 1 | INT16U | ---
I2-Hrm Z1 | 43746 | 1 | INT16U | ---
I2-Hrm Z2 | 43747 | 1 | INT16U | ---
I3-Hrm Z | 43748 | 1 | INT16U | ---
I3-Hrm Z1 | 43749 | 1 | INT16U | ---
I3-Hrm Z2 | 43750 | 1 | INT16U | ---
I-Hrm Z1 | 43751 | 1 | INT16U | ---