## Sheet1
Parameter | Original Address | Modbus Address | Units | Length | Data Type
Meter Name | 30 | 29 | --- | 20 | UTF8
Meter Model | 50 | 49 | --- | 20 | UTF8
Manufacturer | 70 | 69 | --- | 20 | UTF8
Number of Phases | 2014 | 2013 | --- | 1 | INT16U
Number of Wires | 2015 | 2014 | --- | 1 | INT16U
Power System Configuration | 2016 | 2015 | --- | 1 | INT16U
Nominal Frequency | 2017 | 2016 | Hz | 1 | INT16U
Nominal Voltage | 2018 | 2017 | V | 2 | FLOAT32
Nominal Current | 2020 | 2019 | A | 2 | FLOAT32
Nominal Power Factor | 2022 | 2021 | --- | 2 | 4Q_FP_PF
Normal Phase Rotation | 2024 | 2023 | --- | 1 | INT16U
Active Energy Delivered (Into Load) | 2700 | 2699 | kWh | 2 | FLOAT32
Active Energy Received (Out of Load) | 2702 | 2701 | kWh | 2 | FLOAT32
Active Energy Delivered + Received | 2704 | 2703 | kWh | 2 | FLOAT32
Active Energy Delivered- Received | 2706 | 2705 | kWh | 2 | FLOAT32
Reactive Energy Delivered | 2708 | 2707 | kVARh | 2 | FLOAT32
Reactive Energy Received | 2710 | 2709 | kVARh | 2 | FLOAT32
Reactive Energy Delivered + Received | 2712 | 2711 | kVARh | 2 | FLOAT32
Reactive Energy Delivered - Received | 2714 | 2713 | kVARh | 2 | FLOAT32
Apparent Energy Delivered | 2716 | 2715 | kVAh | 2 | FLOAT32
Apparent Energy Received | 2718 | 2717 | kVAh | 2 | FLOAT32
Apparent Energy Delivered + Received | 2720 | 2719 | kVAh | 2 | FLOAT32
Apparent Energy Delivered - Received | 2722 | 2721 | kVAh | 2 | FLOAT32
Current A | 3000 | 2999 | A | 2 | FLOAT32
Current B | 3002 | 3001 | A | 2 | FLOAT32
Current C | 3004 | 3003 | A | 2 | FLOAT32
Current N | 3006 | 3005 | A | 2 | FLOAT32
Current G | 3008 | 3007 | A | 2 | FLOAT32
Current Avg | 3010 | 3009 | A | 2 | FLOAT32
Current Unbalance A | 3012 | 3011 | % | 2 | FLOAT32
Current Unbalance B | 3014 | 3013 | % | 2 | FLOAT32
Current Unbalance C | 3016 | 3015 | % | 2 | FLOAT32
Current Unbalance Worst | 3018 | 3017 | % | 2 | FLOAT32
Voltage A-B | 3020 | 3019 | V | 2 | FLOAT32
Voltage B-C | 3022 | 3021 | V | 2 | FLOAT32
Voltage C-A | 3024 | 3023 | V | 2 | FLOAT32
Voltage L-L Avg | 3026 | 3025 | V | 2 | FLOAT32
Voltage A-N | 3028 | 3027 | V | 2 | FLOAT32
Voltage B-N | 3030 | 3029 | V | 2 | FLOAT32
Voltage C-N | 3032 | 3031 | V | 2 | FLOAT32
Voltage N-G | 3034 | 3033 | V | 2 | FLOAT32
Voltage L-N Avg | 3036 | 3035 | V | 2 | FLOAT32
Voltage Unbalance A-B | 3038 | 3037 | % | 2 | FLOAT32
Voltage Unbalance B-C | 3040 | 3039 | % | 2 | FLOAT32
Voltage Unbalance C-A | 3042 | 3041 | % | 2 | FLOAT32
Voltage Unbalance L-L Worst | 3044 | 3043 | % | 2 | FLOAT32
Voltage Unbalance A-N | 3046 | 3045 | % | 2 | FLOAT32
Voltage Unbalance B-N | 3048 | 3047 | % | 2 | FLOAT32
Voltage Unbalance C-N | 3050 | 3049 | % | 2 | FLOAT32
Voltage Unbalance L-N Worst | 3052 | 3051 | % | 2 | FLOAT32
Active Power A | 3054 | 3053 | kW | 2 | FLOAT32
Active Power B | 3056 | 3055 | kW | 2 | FLOAT32
Active Power C | 3058 | 3057 | kW | 2 | FLOAT32
Active Power Total | 3060 | 3059 | kW | 2 | FLOAT32
Reactive Power A | 3062 | 3061 | kVAR | 2 | FLOAT32
Reactive Power B | 3064 | 3063 | kVAR | 2 | FLOAT32
Reactive Power C | 3066 | 3065 | kVAR | 2 | FLOAT32
Reactive Power Total | 3068 | 3067 | kVAR | 2 | FLOAT32
Apparent Power A | 3070 | 3069 | kVA | 2 | FLOAT32
Apparent Power B | 3072 | 3071 | kVA | 2 | FLOAT32
Apparent Power C | 3074 | 3073 | kVA | 2 | FLOAT32
Apparent Power Total | 3076 | 3075 | kVA | 2 | FLOAT32
Power Factor A | 3078 | 3077 |  | 2 | FLOAT32
Power Factor B | 3080 | 3079 |  | 2 | FLOAT32
Power Factor C | 3082 | 3081 |  | 2 | FLOAT32
Power Factor Total | 3084 | 3083 |  | 2 | FLOAT32
Displacement Power Factor A | 3086 | 3085 |  | 2 | FLOAT32
Displacement Power Factor B | 3088 | 3087 |  | 2 | FLOAT32
Displacement Power Factor C | 3090 | 3089 |  | 2 | FLOAT32
Displacement Power Factor Total | 3092 | 3091 |  | 2 | FLOAT32
Frequency | 3110 | 3109 | Hz | 2 | FLOAT32
Accumulated Energy Reset Date/Time | 3200 | 3199 | --- | 4 | DATETIME
Active Energy Delivered (Into Load) | 3204 | 3203 | Wh | 4 | INT64
Active Energy Received (Out of Load) | 3208 | 3207 | Wh | 4 | INT64
Active Energy Delivered + Received | 3212 | 3211 | Wh | 4 | INT64
Active Energy Delivered- Received | 3216 | 3215 | Wh | 4 | INT64
Reactive Energy Delivered | 3220 | 3219 | VARh | 4 | INT64
Reactive Energy Received | 3224 | 3223 | VARh | 4 | INT64
Reactive Energy Delivered + Received | 3228 | 3227 | VARh | 4 | INT64
Reactive Energy Delivered - Received | 3232 | 3231 | VARh | 4 | INT64
Apparent Energy Delivered | 3236 | 3235 | VAh | 4 | INT64
Apparent Energy Received | 3240 | 3239 | VAh | 4 | INT64
Apparent Energy Delivered + Received | 3244 | 3243 | VAh | 4 | INT64
Apparent Energy Delivered - Received | 3248 | 3247 | VAh | 4 | INT64
P Last Demand | 3764 | 3763 | kW | 2 | FLOAT32
P Present Demand | 3766 | 3765 | kW | 2 | FLOAT32
P Predicted Demand | 3768 | 3767 | kW | 2 | FLOAT32
P Peak Demand | 3770 | 3769 | kW | 2 | FLOAT32
P Peak Demand DateTime | 3772 | 3771 | --- | 4 | DATETIME
kvar Last Demand | 3780 | 3779 | kVAR | 2 | FLOAT32
kvar Present Demand | 3782 | 3781 | kVAR | 2 | FLOAT32
kvar Predicted Demand | 3784 | 3783 | kVAR | 2 | FLOAT32
kvar Peak Demand | 3786 | 3785 | kVAR | 2 | FLOAT32
kvar Peak Demand DateTime | 3788 | 3787 | --- | 4 | DATETIME
kva Last Demand | 3796 | 3795 | kVA | 2 | FLOAT32
kva Present Demand | 3798 | 3797 | kVA | 2 | FLOAT32
kva Predicted Demand | 3800 | 3799 | kVA | 2 | FLOAT32
kva Peak Demand | 3802 | 3801 | kVA | 2 | FLOAT32
kva Peak Demand DateTime | 3804 | 3803 | --- | 4 | DATETIME
Current Last Demand | 3876 | 3875 | A | 2 | FLOAT32
Current Present Demand | 3878 | 3877 | A | 2 | FLOAT32
Current Predicted Demand | 3880 | 3879 | A | 2 | FLOAT32
Current Peak Demand | 3882 | 3881 | A | 2 | FLOAT32
Current Peak Demand DateTime | 3884 | 3883 | --- | 4 | DATETIME
Over Current, Phase | 13523 | 13522 |  | 1 | INT16U
Under Current, Phase | 13524 | 13523 |  | 1 | INT16U
Over Current, Neutral | 13525 | 13524 |  | 1 | INT16U
Over Current, Ground | 13526 | 13525 |  | 1 | INT16U
Over Voltage, L-L | 13527 | 13526 |  | 1 | INT16U
Under Voltage, L-L | 13528 | 13527 |  | 1 | INT16U
Over Voltage, L-N | 13529 | 13528 |  | 1 | INT16U
Under Voltage, L-N | 13530 | 13529 |  | 1 | INT16U
Over Power, Active | 13531 | 13530 |  | 1 | INT16U
Over Power, Reactive | 13532 | 13531 |  | 1 | INT16U
Over Power, Apparent | 13533 | 13532 |  | 1 | INT16U
Lead Power Factor, True | 13534 | 13533 |  | 1 | INT16U
Lag Power Factor, True | 13535 | 13534 |  | 1 | INT16U
Lead Power Factor, Displacement | 13536 | 13535 |  | 1 | INT16U
Lag Power Factor, Displacement | 13537 | 13536 |  | 1 | INT16U
Over Demand, Active Power, Present | 13538 | 13537 |  | 1 | INT16U
Over Demand, Active Power, Last | 13539 | 13538 |  | 1 | INT16U
Over Demand, Active Power, Predicted | 13540 | 13539 |  | 1 | INT16U
Over Demand, Reactive Power, Present | 13541 | 13540 |  | 1 | INT16U
Over Demand, Reactive Power, Last | 13542 | 13541 |  | 1 | INT16U
Over Demand, Reactive Power, Predicted | 13543 | 13542 |  | 1 | INT16U
Over Demand, Apparent Power, Present | 13544 | 13543 |  | 1 | INT16U
Over Demand, Apparent Power, Last | 13545 | 13544 |  | 1 | INT16U
Over Demand, Apparent Power, Predicted | 13546 | 13545 |  | 1 | INT16U
Over Frequency | 13547 | 13546 |  | 1 | INT16U
Under Frequency | 13548 | 13547 |  | 1 | INT16U
Over Voltage Unbalance | 13549 | 13548 |  | 1 | INT16U
Over Voltage Total Harmonic Distortion | 13550 | 13549 |  | 1 | INT16U
Phase Loss | 13551 | 13550 |  | 1 | INT16U
Meter Powerup (Control Power Loss) | 13623 | 13622 | - | 1 | INT16U
Meter Reset | 13624 | 13623 | - | 1 | INT16U
Meter Diagnostic | 13625 | 13624 | - | 1 | INT16U
Phase Reversal | 13626 | 13625 | - | 1 | INT16U
THD Current A | 21300 | 21299 | % | 2 | FLOAT32
THD Current B | 21302 | 21301 | % | 2 | FLOAT32
THD Current C | 21304 | 21303 | % | 2 | FLOAT32
THD Current N | 21306 | 21305 | % | 2 | FLOAT32
THD Current G | 21308 | 21307 | % | 2 | FLOAT32
Total Demand Distortion | 21320 | 21319 | % | 2 | FLOAT32
THD Voltage A-B | 21322 | 21321 | % | 2 | FLOAT32
THD Voltage B-C | 21324 | 21323 | % | 2 | FLOAT32
THD Voltage C-A | 21326 | 21325 | % | 2 | FLOAT32
THD Voltage L-L | 21328 | 21327 | % | 2 | FLOAT32
THD Voltage A-N | 21330 | 21329 | % | 2 | FLOAT32
THD Voltage B-N | 21332 | 21331 | % | 2 | FLOAT32
THD Voltage C-N | 21334 | 21333 | % | 2 | FLOAT32
THD Voltage N-G | 21336 | 21335 | % | 2 | FLOAT32
THD Voltage L-N | 21338 | 21337 | % | 2 | FLOAT32
Voltage A-B, H5 Magnitude, % | 21736 | 21735 | % | 2 | FLOAT32
Voltage A-B, H7 Magnitude, % | 21748 | 21747 | % | 2 | FLOAT32
Voltage B-C, H5 Magnitude, % | 22124 | 22123 | % | 2 | FLOAT32
Voltage B-C, H7 Magnitude, % | 22136 | 22135 | % | 2 | FLOAT32
Voltage C-A, H5 Magnitude, % | 22512 | 22511 | % | 2 | FLOAT32
Voltage C-A, H7 Magnitude, % | 22524 | 22523 | % | 2 | FLOAT32
Voltage A-N, H5 Magnitude, % | 22900 | 22899 | % | 2 | FLOAT32
Voltage A-N, H7 Magnitude, % | 22912 | 22911 | % | 2 | FLOAT32
Voltage B-N, H5 Magnitude, % | 23288 | 23287 | % | 2 | FLOAT32
Voltage B-N, H7 Magnitude, % | 23300 | 23299 | % | 2 | FLOAT32
Voltage C-N, H5 Magnitude, % | 23676 | 23675 | % | 2 | FLOAT32
Voltage C-N, H7 Magnitude, % | 23688 | 23687 | % | 2 | FLOAT32
Current A, H3 Magnitude, % | 24440 | 24439 | % | 2 | FLOAT32
Current A, H5 Magnitude, % | 24452 | 24451 | % | 2 | FLOAT32
Current A, H7 Magnitude, % | 24464 | 24463 | % | 2 | FLOAT32
Current B, H3 Magnitude, % | 24828 | 24827 | % | 2 | FLOAT32
Current B, H5 Magnitude, % | 24840 | 24839 | % | 2 | FLOAT32
Current B, H7 Magnitude, % | 24852 | 24851 | % | 2 | FLOAT32
Current C, H3 Magnitude, % | 25216 | 25215 | % | 2 | FLOAT32
Current C, H5 Magnitude, % | 25228 | 25227 | % | 2 | FLOAT32
Current C, H7 Magnitude, % | 25240 | 25239 | % | 2 | FLOAT32
Min Current A | 27218 | 27217 | A | 2 | FLOAT32
Min Current B | 27220 | 27219 | A | 2 | FLOAT32
Min Current C | 27222 | 27221 | A | 2 | FLOAT32
Min Current N | 27224 | 27223 | A | 2 | FLOAT32
Min Current G | 27226 | 27225 | A | 2 | FLOAT32
Min Current Avg | 27228 | 27227 | A | 2 | FLOAT32
Min Current Unbalance A | 27230 | 27229 | % | 2 | FLOAT32
Min Current Unbalance B | 27232 | 27231 | % | 2 | FLOAT32
Min Current Unbalance C | 27234 | 27233 | % | 2 | FLOAT32
Min Current Unbalance Worst | 27236 | 27235 | % | 2 | FLOAT32
Min Voltage A-B | 27238 | 27237 | V | 2 | FLOAT32
Min Voltage B-C | 27240 | 27239 | V | 2 | FLOAT32
Min Voltage C-A | 27242 | 27241 | V | 2 | FLOAT32
Min Voltage L-L Avg | 27244 | 27243 | V | 2 | FLOAT32
Min Voltage A-N | 27246 | 27245 | V | 2 | FLOAT32
Min Voltage B-N | 27248 | 27247 | V | 2 | FLOAT32
Min Voltage C-N | 27250 | 27249 | V | 2 | FLOAT32
Min Voltage N-G | 27252 | 27251 | V | 2 | FLOAT32
Min Voltage L-N Avg | 27254 | 27253 | V | 2 | FLOAT32
Min Voltage Unbalance A-B | 27256 | 27255 | % | 2 | FLOAT32
Min Voltage Unbalance B-C | 27258 | 27257 | % | 2 | FLOAT32
Min Voltage Unbalance C-A | 27260 | 27259 | % | 2 | FLOAT32
Min Voltage Unbalance L-L Worst | 27262 | 27261 | % | 2 | FLOAT32
Min Voltage Unbalance A-N | 27264 | 27263 | % | 2 | FLOAT32
Min Voltage Unbalance B-N | 27266 | 27265 | % | 2 | FLOAT32
Min Voltage Unbalance C-N | 27268 | 27267 | % | 2 | FLOAT32
Min Voltage Unbalance L-N Worst | 27270 | 27269 | % | 2 | FLOAT32
Min Active Power A | 27272 | 27271 | kW | 2 | FLOAT32
Min Active Power B | 27274 | 27273 | kW | 2 | FLOAT32
Min Active Power C | 27276 | 27275 | kW | 2 | FLOAT32
Min Active Power Total | 27278 | 27277 | kW | 2 | FLOAT32
Min Reactive Power A | 27280 | 27279 | kVAR | 2 | FLOAT32
Min Reactive Power B | 27282 | 27281 | kVAR | 2 | FLOAT32
Min Reactive Power C | 27284 | 27283 | kVAR | 2 | FLOAT32
Min Reactive Power Total | 27286 | 27285 | kVAR | 2 | FLOAT32
Min Apparent Power A | 27288 | 27287 | kVA | 2 | FLOAT32
Min Apparent Power B | 27290 | 27289 | kVA | 2 | FLOAT32
Min Apparent Power C | 27292 | 27291 | kVA | 2 | FLOAT32
Min Apparent Power Total | 27294 | 27293 | kVA | 2 | FLOAT32
Min Power Factor A | 27306 | 27305 |  | 2 | 4Q_FP_PF
Min Power Factor B | 27308 | 27307 |  | 2 | 4Q_FP_PF
Min Power Factor C | 27310 | 27309 |  | 2 | 4Q_FP_PF
Min Power Factor Total | 27312 | 27311 |  | 2 | 4Q_FP_PF
Min Displacement Power Factor A | 27314 | 27313 |  | 2 | 4Q_FP_PF
Min Displacement Power Factor B | 27316 | 27315 |  | 2 | 4Q_FP_PF
Min Displacement Power Factor C | 27318 | 27317 |  | 2 | 4Q_FP_PF
Min Displacement PF Total | 27320 | 27319 |  | 2 | 4Q_FP_PF
Min THD Current A | 27338 | 27337 | % | 2 | FLOAT32
Min THD Current B | 27340 | 27339 | % | 2 | FLOAT32
Min THD Current C | 27342 | 27341 | % | 2 | FLOAT32
Min THD Current N | 27344 | 27343 | % | 2 | FLOAT32
Min THD Current G | 27346 | 27345 | % | 2 | FLOAT32
Min Total Demand Distortion | 27358 | 27357 | % | 2 | FLOAT32
Min THD Voltage A-B | 27360 | 27359 | % | 2 | FLOAT32
Min THD Voltage B-C | 27362 | 27361 | % | 2 | FLOAT32
Min THD Voltage C-A | 27364 | 27363 | % | 2 | FLOAT32
Min THD Voltage L-L Avg | 27366 | 27365 | % | 2 | FLOAT32
Min THD Voltage A-N | 27368 | 27367 | % | 2 | FLOAT32
Min THD Voltage B-N | 27370 | 27369 | % | 2 | FLOAT32
Min THD Voltage C-N | 27372 | 27371 | % | 2 | FLOAT32
Min THD Voltage N-G | 27374 | 27373 | % | 2 | FLOAT32
Min THD Voltage L-N Avg | 27376 | 27375 | % | 2 | FLOAT32
Min Frequency | 27616 | 27615 | Hz | 2 | FLOAT32
Max Current A | 27694 | 27693 | A | 2 | FLOAT32
Max Current B | 27696 | 27695 | A | 2 | FLOAT32
Max Current C | 27698 | 27697 | A | 2 | FLOAT32
Max Current N | 27700 | 27699 | A | 2 | FLOAT32
Max Current G | 27702 | 27701 | A | 2 | FLOAT32
Max Current Avg | 27704 | 27703 | A | 2 | FLOAT32
Max Current Unbalance A | 27706 | 27705 | % | 2 | FLOAT32
Max Current Unbalance B | 27708 | 27707 | % | 2 | FLOAT32
Max Current Unbalance C | 27710 | 27709 | % | 2 | FLOAT32
Max Current Unbalance Worst | 27712 | 27711 | % | 2 | FLOAT32
Max Voltage A-B | 27714 | 27713 | V | 2 | FLOAT32
Max Voltage B-C | 27716 | 27715 | V | 2 | FLOAT32
Max Voltage C-A | 27718 | 27717 | V | 2 | FLOAT32
Max Voltage L-L Avg | 27720 | 27719 | V | 2 | FLOAT32
Max Voltage A-N | 27722 | 27721 | V | 2 | FLOAT32
Max Voltage B-N | 27724 | 27723 | V | 2 | FLOAT32
Max Voltage C-N | 27726 | 27725 | V | 2 | FLOAT32
Max Voltage, N-G | 27728 | 27727 | V | 2 | FLOAT32
Max Voltage L-N Avg | 27730 | 27729 | V | 2 | FLOAT32
Max Voltage Unbalance A-B | 27732 | 27731 | % | 2 | FLOAT32
Max Voltage Unbalance B-C | 27734 | 27733 | % | 2 | FLOAT32
Max Voltage Unbalance C-A | 27736 | 27735 | % | 2 | FLOAT32
Max Voltage Unbalance L-L Worst | 27738 | 27737 | % | 2 | FLOAT32
Max Voltage Unbalance A-N | 27740 | 27739 | % | 2 | FLOAT32
Max Voltage Unbalance B-N | 27742 | 27741 | % | 2 | FLOAT32
Max Voltage Unbalance C-N | 27744 | 27743 | % | 2 | FLOAT32
Max Voltage Unbalance L-N Worst | 27746 | 27745 | % | 2 | FLOAT32
Max Active Power A | 27748 | 27747 | kW | 2 | FLOAT32
Max Active Power B | 27750 | 27749 | kW | 2 | FLOAT32
Max Active Power C | 27752 | 27751 | kW | 2 | FLOAT32
Max Active Power Total | 27754 | 27753 | kW | 2 | FLOAT32
Max Reactive Power A | 27756 | 27755 | kVAR | 2 | FLOAT32
Max Reactive Power B | 27758 | 27757 | kVAR | 2 | FLOAT32
Max Reactive Power C | 27760 | 27759 | kVAR | 2 | FLOAT32
Max Reactive Power Total | 27762 | 27761 | kVAR | 2 | FLOAT32
Max Apparent Power A | 27764 | 27763 | kVA | 2 | FLOAT32
Max Apparent Power B | 27766 | 27765 | kVA | 2 | FLOAT32
Max Apparent Power C | 27768 | 27767 | kVA | 2 | FLOAT32
Max Apparent Power Total | 27770 | 27769 | kVA | 2 | FLOAT32
Max Power Factor A | 27782 | 27781 | --- | 2 | 4Q_FP_PF
Max Power Factor B | 27784 | 27783 | --- | 2 | 4Q_FP_PF
Max Power Factor C | 27786 | 27785 | --- | 2 | 4Q_FP_PF
Max Power Factor Total | 27788 | 27787 | --- | 2 | 4Q_FP_PF
Max Displacement Power Factor A | 27790 | 27789 | --- | 2 | 4Q_FP_PF
Max Displacement Power Factor B | 27792 | 27791 | --- | 2 | 4Q_FP_PF
Max Displacement Power Factor C | 27794 | 27793 | --- | 2 | 4Q_FP_PF
Max Displacement PF Total | 27796 | 27795 | --- | 2 | 4Q_FP_PF
Max THD Current A | 27814 | 27813 | % | 2 | FLOAT32
Max THD Current B | 27816 | 27815 | % | 2 | FLOAT32
Max THD Current C | 27818 | 27817 | % | 2 | FLOAT32
Max THD Current N | 27820 | 27819 | % | 2 | FLOAT32
Max THD Current G | 27822 | 27821 | % | 2 | FLOAT32
Max THD Voltage A-B | 27836 | 27835 | % | 2 | FLOAT32
Max THD Voltage B-C | 27838 | 27837 | % | 2 | FLOAT32
Max THD Voltage C-A | 27840 | 27839 | % | 2 | FLOAT32
Max THD Voltage L-L | 27842 | 27841 | % | 2 | FLOAT32
Max THD Voltage A-N | 27844 | 27843 | % | 2 | FLOAT32
Max THD Voltage B-N | 27846 | 27845 | % | 2 | FLOAT32
Max THD Voltage C-N | 27848 | 27847 | % | 2 | FLOAT32
Max THD Voltage N-G | 27850 | 27849 | % | 2 | FLOAT32
Max THD Voltage L-N | 27852 | 27851 | % | 2 | FLOAT32
Max Frequency | 28092 | 28091 | Hz | 2 | FLOAT32